Author: Sheard Goodwin

First Revision: 7-25-2001

Last Revision: 6-15-2004

Label Standard For Connecting Jumpers In General Jumpers should be labeled on each end within 6 inches of the termination. Each label will have two lines of writing. Each line of writing will detail one of the termination points of the cable. From this, a technician can tell where each end of a jumper should be plugged in by looking at only one end of the jumper. The labels to be affixed to jumpers do not communicate anything about the nature of the jumper itself. The sole purpose of the label is to communicate the location of the equipment and the port on that equipment where that jumper is terminated. The labels themselves consist of distinct pieces of information separated by a period. If a piece of equipment is wall mounted a w will be entered into the rack number location. These pieces of information read like a map from the general to the specific from left to right : rack.equipment.port Termination points 1) Termination of a jumper in a fiber panel is labeled solely through the use of numbers. The rack number is followed by the fpl number and finally the module and port numbers in a format of #.#.#/# This keeps the identifying label short and specific. 1.1.1/5 : This entry on a label points to a termination in Rack #1, FPL1, module 1 and port 5. 2) Termination of a jumper in a copper patch panel will be labeled with the letter of the panel. The rack number is followed by the panel letter and finally by the port number in a format of #.a.# Again, this communicates the necessary information in as succint a manner as possible. 1.a.1 : This entry on a label points to a termination in Rack #1, copper patch panel A and port 1 3) Termination of a jumper in a piece of electronics equipment uses the infrastructure name for identification. In detailing the equipment portion of the label it is necessary to use the final component of the infrastructure name and the index number. 1.esw01.1/1 : This entry on a label points to a termination in Rack #1, switch #1 and blade 1, port 1 Note : blade 0 on a switch refers to a port on the switch itself and not attached to any additional cards or modules. 4) Termination of a jumper in server uses a shortened version of the DNS name of the device in the jumper label. This shortened version is not standard but allows the name to fit on the label. For example, ids-aesens may be abbrevicated ids-ae. A Complete Label A label should have two lines of writing that detail the two termination points of the jumper. All of the examples above only detail one end of the termination. A complete label that might be found on both ends of a jumper might appear as follows. w.a.4 1.esw01.0/4 This jumper runs from port 4 of copper panel a to port 4 of switch #2. The copper panel is located on the wall while the workgroup switch is located in rack #1. 7.sh1.2/1 8.esw01.1/2 This jumper runs from shomiti device #1 in rack #7 to switch #1 in rack #8. It connects to module 2, port 1 on the shomiti and module 1, port 2 on the switch. 1.1.1/2 2.esw01.1/1 This jumper runs from rack #1, FPL1, module 1, port 2 over to rack #2, switch #1, blade 1 and port 1. A Final Note Should it become necessary during the course of labeling older installations to label jumpers that run between rooms or buildings these additional identifiers can be added on to the front of the entry. As always, entries are read from the general to the specific from left to right so the order should be building.room.rack.equipment.port Again, these are not acceptable for new installations. For connections between rooms and buildings permanent cables should be run. 0038.BA.1.a.4 0031.1A.1.esw01.0/2 This jumper runs between building 38 and building 31. In building 38 the jumper terminates in Telecomm room BA, rack #1, patch panel A and port 4. In building 31 the jumper terminates in Telecom room 1A, rack #1, switch #1, module #0, port 2.